## Start Here
Energy Use and Demand Charge Tracker
| Read this first: what the workbook does and how to use it. |  |  |  | mfgcalcs.com
Energy Use and Demand Charge Tracker
Log monthly electricity bills and sub-meter readings, and see cost, peak and billing demand, ratchet charges, load factor and energy per unit of output.
For: Plant and facility managers, energy managers, maintenance engineers and plant controllers.
Version 1.0.0 · updated 15 October 2026
Quick start
| 1. | On Setup, type your plant name, currency, output unit and targets, then the demand part of your tariff: rate per kW, ratchet, contract demand and fixed fees.
| 2. | On Monthly Bills, add one row per bill: the month, days billed, kWh, peak kW, the energy, demand and other charges, and the month's production.
| 3. | Read the Check column: it flags a demand charge that does not match your tariff, duplicate months and impossible load factors.
| 4. | On Sub-meters, add each meter's kWh per month to see where the energy goes (optional).
| 5. | Open the Dashboard; change the '12 months ending' date to look at any year.
What is in this workbook
|  | Start Here | Read this first: what the workbook does and how to use it.
|  | Setup | Your plant, currency, output unit, targets, the demand part of your tariff and the sub-meter list.
|  | Monthly Bills | One row per electricity bill: energy, peak demand, charges and production.
|  | Sub-meters | Energy per sub-meter per month: where the electricity goes.
|  | Dashboard | Energy cost, peak and billing demand, ratchet charges, load factor, intensity and end uses for any 12 months.
|  | Method | How every number is calculated, with assumptions, limits and sources.
|  | Verify | Self-check: the workbook's formulas recomputed on fixed inputs against an independent reference.
Colour key
|  | Input | Yellow cells are yours: type a value or pick from the list. Each one says what it accepts when you click it.
|  | Calculated | Blue cells are formulas. They update as you type; overwrite one and that row stops calculating.
|  | Note | Grey boxes are guidance and labelled example data.
|  | Status words | On target / PASS / OK | Near target / Check | Below target / FAIL
Status is always written in words; the colour only repeats it, so the workbook reads the same in black-and-white print and for colour-blind readers.
Self-check and links
|  | Self-check | PASS | 19 of 19 checks pass
The Verify sheet recomputes this workbook's formulas on fixed test inputs and compares them with an independent reference calculation. PASS means every check agreed when you opened the file.
|  | Run it live | Utility Demand Charge Calculator on mfgcalcs.com
|  | Latest version | mfgcalcs.com/templates/energy-monitoring
|  | More free templates | mfgcalcs.com/templates
|  | Version | 1.0.0 (updated 15 October 2026)
About the example data
Every number already in this workbook is example data for Ridgeway Castings, a fictional business invented for this template, so the dashboard and charts show something meaningful on day one. It covers an aluminium die-casting foundry with electric melting: 24 monthly bills (October 2024 to September 2026) and 12 months of sub-meter readings, generated from a fixed seed. Tariff values are examples, not any utility's prices. To clear it: on each working sheet, select the example rows of the table, right-click and choose Delete > Table Rows. The formulas stay, and every new row you type below the table picks them up.
Good to know
| • | Sheets Start Here, Dashboard, Method, Verify are protected without a password so formulas and layout are not overwritten by accident. To change them: Review > Unprotect Sheet.
| • | Setup and the working sheets are not protected, so tables grow as you add rows.
| • | Works in Excel 2016 and later, Microsoft 365, LibreOffice 24 and Google Sheets (File > Import). No macros, no external links, no add-ins.
| • | Money is shown in the currency you type on Setup; no exchange rates are applied.
Free from MFG Calcs - keep this credit when you share it.
Engineering estimates for planning and improvement work. Verify the results against your own process, data and standards before you rely on them.

## Setup
Energy Use and Demand Charge Tracker
| Your plant, currency, output unit, targets, the demand part of your tariff and the sub-meter list. |  | mfgcalcs.com
Plant and targets
| Plant name | Ridgeway Castings (example)
| Currency label | USD
| Unit of output | t
| Energy intensity target | 1400 | kWh/t
| Load factor target | 65%
Targets are yours to set; nothing in this workbook assumes an industry benchmark. 'Near target' means within 5% of the target: up to 1,470 kWh/t against a 1,400 kWh/t intensity target.
Demand charge rules from your tariff
Copy these from your electricity tariff or contract. They let the workbook work out the billing demand and the demand charge you should have been billed, and flag bills that do not match. The example values are illustrative, not any utility's prices.
| Demand charge rate | 14.5 | USD/kW
| Share of billing demand charged | 100%
| Fixed demand-related fees | 450 | USD/bill
| Demand ratchet | 80%
| Ratchet look-back | 11 | months
| Contract (sanctioned) demand | 0 | kW
| Minimum billing share of contract demand | 75%
| Bill check tolerance | 2%
Sub-meters
One row per sub-meter or end use. The Sub-meters log's dropdown reads this list; the Dashboard shows each meter's share of the billed energy and the unmetered rest.
Sub-meters (example)
| Meter | End use | Notes
| Melting furnaces | Process heat | Two induction furnaces and holding furnaces
| Die casting cells | Machines | Six cold-chamber machines, trim presses
| Compressed air | Utilities | Three screw compressors
| HVAC and fume extraction | Building | Make-up air, extraction fans
| Lighting and offices | Building | High-bay lighting, offices

## Monthly Bills
Energy Use and Demand Charge Tracker
| One row per electricity bill: energy, peak demand, charges and production. | [19 empty] | mfgcalcs.com
Example data for Ridgeway Castings (fictional); the March 2026 bill is wrong on purpose, to show the Check column at work. Replace it with your own: select the example rows, right-click, Delete > Table Rows.
[5 empty] | USD | USD | USD | t | USD | % | USD/kWh |  |  | USD | USD | USD | kWh/t | USD/t
| Month | Days | Energy (kWh) | Peak demand (kW) | Energy charges | Demand charges | Other charges | Production | Total bill | Load factor | Blended cost | Ratchet floor (kW) | Billing demand (kW) | Expected demand charge | Variance vs tariff | Paid for past peaks | Energy intensity | Cost per unit | Intensity status | Check | Notes
| 2024-10-01 | 31 | 915870 | 2045 | 69631.41 | 30102.5 | 3242.02 | 619.9 | 102975.93 | 60.2% | 0.11244 | 0 | 2045 | 30102.5 | 0 | 0 | 1477.448 | 166.117 | Above target | OK
| 2024-11-01 | 30 | 915130 | 2005 | 69773.8 | 29522.5 | 3228.89 | 631.1 | 102525.19 | 63.39% | 0.11203 | 1636 | 2005 | 29522.5 | 0 | 0 | 1450.0555 | 162.4547 | Near target | OK
| 2024-12-01 | 31 | 809910 | 1820 | 61661.93 | 26840 | 2905.06 | 511.5 | 91406.99 | 59.81% | 0.11286 | 1636 | 1820 | 26840 | 0 | 0 | 1583.4018 | 178.7038 | Above target | OK
| 2025-01-01 | 31 | 917430 | 2780 | 69554.67 | 40760 | 3559.44 | 623 | 113874.11 | 44.36% | 0.12412 | 1636 | 2780 | 40760 | 0 | 0 | 1472.6003 | 182.7835 | Above target | OK | Two furnaces cold-started together after the shutdown
| 2025-02-01 | 28 | 913530 | 2025 | 69627.11 | 32698 | 3319.75 | 637.1 | 105644.86 | 67.13% | 0.11564 | 2224 | 2224 | 32698 | 0 | 2885.5 | 1433.8879 | 165.8215 | Near target | OK
| 2025-03-01 | 31 | 899340 | 2065 | 68113.88 | 32698 | 3274.36 | 606.2 | 104086.24 | 58.54% | 0.11574 | 2224 | 2224 | 32698 | 0 | 2305.5 | 1483.5698 | 171.7028 | Above target | OK
| 2025-04-01 | 30 | 913790 | 1995 | 69767.79 | 32698 | 3323.97 | 616.7 | 105789.76 | 63.62% | 0.11577 | 2224 | 2224 | 32698 | 0 | 3320.5 | 1481.7415 | 171.5417 | Above target | OK
| 2025-05-01 | 31 | 904150 | 2025 | 68829.39 | 32698 | 3295.82 | 602.1 | 104823.21 | 60.01% | 0.11594 | 2224 | 2224 | 32698 | 0 | 2885.5 | 1501.6609 | 174.096 | Above target | OK
| 2025-06-01 | 30 | 921180 | 2005 | 69662.14 | 32698 | 3320.8 | 618.7 | 105680.94 | 63.81% | 0.11472 | 2224 | 2224 | 32698 | 0 | 3175.5 | 1488.8961 | 170.8113 | Above target | OK
| 2025-07-01 | 31 | 892120 | 2015 | 67786.84 | 32698 | 3264.55 | 602 | 103749.39 | 59.51% | 0.1163 | 2224 | 2224 | 32698 | 0 | 3030.5 | 1481.9269 | 172.3412 | Above target | OK
| 2025-08-01 | 31 | 764890 | 1865 | 57938.68 | 32698 | 2969.1 | 472.7 | 93605.78 | 55.12% | 0.12238 | 2224 | 2224 | 32698 | 0 | 5205.5 | 1618.1299 | 198.0237 | Above target | OK
| 2025-09-01 | 30 | 893990 | 1965 | 68088.15 | 32698 | 3273.58 | 599 | 104059.73 | 63.19% | 0.1164 | 2224 | 2224 | 32698 | 0 | 3755.5 | 1492.4708 | 173.7224 | Above target | OK
| 2025-10-01 | 31 | 928230 | 2080 | 70649.48 | 32698 | 3350.42 | 629.2 | 106697.9 | 59.98% | 0.11495 | 2224 | 2224 | 32698 | 0 | 2088 | 1475.2543 | 169.5771 | Above target | OK
| 2025-11-01 | 30 | 914320 | 2035 | 69518.09 | 32698 | 3316.48 | 623 | 105532.57 | 62.4% | 0.11542 | 2224 | 2224 | 32698 | 0 | 2740.5 | 1467.6083 | 169.3942 | Near target | OK
| 2025-12-01 | 31 | 827570 | 1960 | 62885.61 | 32698 | 3117.51 | 534 | 98701.12 | 56.75% | 0.11927 | 2224 | 2224 | 32698 | 0 | 3828 | 1549.7566 | 184.8336 | Above target | OK
| 2026-01-01 | 31 | 925410 | 2310 | 75285.44 | 33945 | 3526.91 | 615.3 | 112757.35 | 53.85% | 0.12185 | 1664 | 2310 | 33945 | 0 | 0 | 1503.998 | 183.2559 | Above target | OK | Staggered furnace starts after the shutdown
| 2026-02-01 | 28 | 909230 | 2005 | 74456.65 | 29522.5 | 3369.37 | 634 | 107348.52 | 67.48% | 0.11807 | 1848 | 2005 | 29522.5 | 0 | 0 | 1434.1167 | 169.3194 | Near target | OK
| 2026-03-01 | 31 | 918970 | 2005 | 74755.51 | 31234.81 | 3429.71 | 614.5 | 109420.03 | 61.6% | 0.11907 | 1848 | 2005 | 29522.5 | 1712.31 | 0 | 1495.476 | 178.0635 | Above target | Demand charge above tariff | Demand charge does not match the tariff: queried with the utility
| 2026-04-01 | 30 | 879350 | 2065 | 71721.58 | 30392.5 | 3313.42 | 620.4 | 105427.5 | 59.14% | 0.11989 | 1848 | 2065 | 30392.5 | 0 | 0 | 1417.392 | 169.9347 | Near target | OK
| 2026-05-01 | 31 | 881870 | 2015 | 72213.34 | 29667.5 | 3306.43 | 618.4 | 105187.27 | 58.82% | 0.11928 | 1848 | 2015 | 29667.5 | 0 | 0 | 1426.0511 | 170.0958 | Near target | OK
| 2026-06-01 | 30 | 891730 | 2055 | 72975.81 | 30247.5 | 3346.7 | 633.1 | 106570.01 | 60.27% | 0.11951 | 1848 | 2055 | 30247.5 | 0 | 0 | 1408.5137 | 168.3305 | Near target | OK
| 2026-07-01 | 31 | 909740 | 2090 | 73961.75 | 30755 | 3391.5 | 632.1 | 108108.25 | 58.51% | 0.11883 | 1848 | 2090 | 30755 | 0 | 0 | 1439.2343 | 171.0303 | Near target | OK
| 2026-08-01 | 31 | 735620 | 1775 | 59986.97 | 27246 | 2866.99 | 475.8 | 90099.96 | 55.7% | 0.12248 | 1848 | 1848 | 27246 | 0 | 1058.5 | 1546.0698 | 189.3652 | Above target | OK
| 2026-09-01 | 30 | 877680 | 2030 | 71720.04 | 29885 | 3298.15 | 611.4 | 104903.19 | 60.05% | 0.11952 | 1848 | 2030 | 29885 | 0 | 0 | 1435.525 | 171.5787 | Near target | OK

## Sub-meters
Energy Use and Demand Charge Tracker
| Energy per sub-meter per month: where the electricity goes. |  |  |  |  | mfgcalcs.com
Example data for Ridgeway Castings (fictional): five sub-meters from October 2025. Replace it with your own readings.
| Month | Meter | Energy (kWh) | Share of bill | Check | Notes
| 2025-10-01 | Melting furnaces | 487670 | 52.54% | OK
| 2025-10-01 | Die casting cells | 162660 | 17.52% | OK
| 2025-10-01 | Compressed air | 116380 | 12.54% | OK
| 2025-10-01 | HVAC and fume extraction | 81010 | 8.727% | OK
| 2025-10-01 | Lighting and offices | 27940 | 3.01% | OK
| 2025-11-01 | Melting furnaces | 480260 | 52.53% | OK
| 2025-11-01 | Die casting cells | 166190 | 18.18% | OK
| 2025-11-01 | Compressed air | 111310 | 12.17% | OK
| 2025-11-01 | HVAC and fume extraction | 75560 | 8.264% | OK
| 2025-11-01 | Lighting and offices | 27630 | 3.022% | OK
| 2025-12-01 | Melting furnaces | 417480 | 50.45% | OK
| 2025-12-01 | Die casting cells | 147870 | 17.87% | OK
| 2025-12-01 | Compressed air | 103600 | 12.52% | OK
| 2025-12-01 | HVAC and fume extraction | 69920 | 8.449% | OK
| 2025-12-01 | Lighting and offices | 24390 | 2.947% | OK
| 2026-01-01 | Melting furnaces | 489000 | 52.84% | OK
| 2026-01-01 | Die casting cells | 162090 | 17.52% | OK
| 2026-01-01 | Compressed air | 118100 | 12.76% | OK
| 2026-01-01 | HVAC and fume extraction | 76510 | 8.268% | OK
| 2026-01-01 | Lighting and offices | 28000 | 3.026% | OK
| 2026-02-01 | Melting furnaces | 466720 | 51.33% | OK
| 2026-02-01 | Die casting cells | 165080 | 18.16% | OK
| 2026-02-01 | Compressed air | 116860 | 12.85% | OK
| 2026-02-01 | HVAC and fume extraction | 76720 | 8.438% | OK
| 2026-02-01 | Lighting and offices | 26770 | 2.944% | OK
| 2026-03-01 | Melting furnaces | 464510 | 50.55% | OK
| 2026-03-01 | Die casting cells | 165690 | 18.03% | OK
| 2026-03-01 | Compressed air | 111720 | 12.16% | OK
| 2026-03-01 | HVAC and fume extraction | 80210 | 8.728% | OK
| 2026-03-01 | Lighting and offices | 27380 | 2.979% | OK
| 2026-04-01 | Melting furnaces | 458110 | 52.1% | OK
| 2026-04-01 | Die casting cells | 162070 | 18.43% | OK
| 2026-04-01 | Compressed air | 90640 | 10.31% | OK
| 2026-04-01 | HVAC and fume extraction | 76790 | 8.733% | OK
| 2026-04-01 | Lighting and offices | 26630 | 3.028% | OK
| 2026-05-01 | Melting furnaces | 453440 | 51.42% | OK
| 2026-05-01 | Die casting cells | 162590 | 18.44% | OK
| 2026-05-01 | Compressed air | 91500 | 10.38% | OK
| 2026-05-01 | HVAC and fume extraction | 73810 | 8.37% | OK
| 2026-05-01 | Lighting and offices | 27080 | 3.071% | OK
| 2026-06-01 | Melting furnaces | 455770 | 51.11% | OK
| 2026-06-01 | Die casting cells | 159770 | 17.92% | OK
| 2026-06-01 | Compressed air | 95580 | 10.72% | OK
| 2026-06-01 | HVAC and fume extraction | 93930 | 10.53% | OK
| 2026-06-01 | Lighting and offices | 27310 | 3.063% | OK
| 2026-07-01 | Melting furnaces | 460770 | 50.65% | OK
| 2026-07-01 | Die casting cells | 159390 | 17.52% | OK
| 2026-07-01 | Compressed air | 99030 | 10.89% | OK
| 2026-07-01 | HVAC and fume extraction | 93460 | 10.27% | OK
| 2026-07-01 | Lighting and offices | 27970 | 3.075% | OK
| 2026-08-01 | Melting furnaces | 389950 | 53.01% | OK
| 2026-08-01 | Die casting cells | 131540 | 17.88% | OK
| 2026-08-01 | Compressed air | 77630 | 10.55% | OK
| 2026-08-01 | HVAC and fume extraction | 79520 | 10.81% | OK
| 2026-08-01 | Lighting and offices | 22440 | 3.05% | OK
| 2026-09-01 | Melting furnaces | 459550 | 52.36% | OK
| 2026-09-01 | Die casting cells | 158630 | 18.07% | OK
| 2026-09-01 | Compressed air | 93610 | 10.67% | OK
| 2026-09-01 | HVAC and fume extraction | 76510 | 8.717% | OK
| 2026-09-01 | Lighting and offices | 26740 | 3.047% | OK

## Dashboard
Energy Use and Demand Charge Tracker
| Energy cost, peak and billing demand, ratchet charges, load factor, intensity and end uses for any 12 months. | [8 empty] | mfgcalcs.com
| 12 months ending |  |  |  |  | Bills in these months |  | 12
| First month shown |  | 2025-10-01 |  |  | Last month shown |  | 2026-09-01
Money in USD; output in t. Leave the date blank to see the latest 12 bills.
| ELECTRICITY COST (USD) |  | DEMAND CHARGES SHARE |  |  | PAID FOR PAST PEAKS (USD) |  |  | HIGHEST PEAK DEMAND (KW)
| 1260753.67 |  | 29.43% |  |  | 9715 |  |  | 2310
| Total of the bills shown |  | Demand charges / total bill |  |  | Ratchet or contract minimum above own peak |  |  | In the 12 months shown
| ENERGY INTENSITY (KWH/T) |  | LOAD FACTOR |  |  | BLENDED COST (USD/KWH) |  |  | ENERGY USED (MWH)
| 1463.8071 |  | 59.44% |  |  | 0.11894 |  |  | 10599.72
| 1400 |  | 65% |  |  | Total bill / kWh |  |  | In the 12 months shown
| Near target |  | Below target
By month
| Month | Energy (kWh) | Peak demand (kW) | Billing demand (kW) | Energy charges | Demand charges | Other charges | Total bill | Load factor | Energy intensity | Intensity target
[5 empty] | USD | USD | USD | USD | % | kWh/t | kWh/t
| 2025-10-01 | 928230 | 2080 | 2224 | 70649.48 | 32698 | 3350.42 | 106697.9 | 59.98% | 1475.2543 | 1400
| 2025-11-01 | 914320 | 2035 | 2224 | 69518.09 | 32698 | 3316.48 | 105532.57 | 62.4% | 1467.6083 | 1400
| 2025-12-01 | 827570 | 1960 | 2224 | 62885.61 | 32698 | 3117.51 | 98701.12 | 56.75% | 1549.7566 | 1400
| 2026-01-01 | 925410 | 2310 | 2310 | 75285.44 | 33945 | 3526.91 | 112757.35 | 53.85% | 1503.998 | 1400
| 2026-02-01 | 909230 | 2005 | 2005 | 74456.65 | 29522.5 | 3369.37 | 107348.52 | 67.48% | 1434.1167 | 1400
| 2026-03-01 | 918970 | 2005 | 2005 | 74755.51 | 31234.81 | 3429.71 | 109420.03 | 61.6% | 1495.476 | 1400
| 2026-04-01 | 879350 | 2065 | 2065 | 71721.58 | 30392.5 | 3313.42 | 105427.5 | 59.14% | 1417.392 | 1400
| 2026-05-01 | 881870 | 2015 | 2015 | 72213.34 | 29667.5 | 3306.43 | 105187.27 | 58.82% | 1426.0511 | 1400
| 2026-06-01 | 891730 | 2055 | 2055 | 72975.81 | 30247.5 | 3346.7 | 106570.01 | 60.27% | 1408.5137 | 1400
| 2026-07-01 | 909740 | 2090 | 2090 | 73961.75 | 30755 | 3391.5 | 108108.25 | 58.51% | 1439.2343 | 1400
| 2026-08-01 | 735620 | 1775 | 1848 | 59986.97 | 27246 | 2866.99 | 90099.96 | 55.7% | 1546.0698 | 1400
| 2026-09-01 | 877680 | 2030 | 2030 | 71720.04 | 29885 | 3298.15 | 104903.19 | 60.05% | 1435.525 | 1400
| Where the energy goes (12 months shown) | [5 empty] | Unmetered energy (same months)
| Sub-meter | Energy (kWh) | Share of billed energy | Energy intensity | Cost at blended rate (est.) |  | Metered by the sub-meters |  |  | 9886990 | kWh
|  |  | % | kWh/t | USD |  | Unmetered and losses |  |  | 712730 | kWh
| Melting furnaces | 5483230 | 51.73% | 757.2267 | 652187.2602 |  | Unmetered share of billed energy |  |  | 6.724% | %
| Die casting cells | 1903570 | 17.96% | 262.8805 | 226414.7415
| Compressed air | 1225960 | 11.57% | 169.3034 | 145818.3395
| HVAC and fume extraction | 953950 | 9% | 131.7392 | 113464.8805
| Lighting and offices | 320280 | 3.022% | 44.2302 | 38094.7974
The Dashboard shows the 5 sub-meters of the Setup list. If you add more, extend the 'Where the energy goes' block (see Method) or they will not appear here; the unmetered line still counts them.

## Method
Energy Use and Demand Charge Tracker
| How every number is calculated, with assumptions, limits and sources. |  | mfgcalcs.com
What this workbook calculates
An electricity bill has two big parts: energy, priced per kWh used, and demand, priced per kW of the highest short-interval demand in the month. This workbook rebuilds the demand part from your tariff's rules, so you can see what each peak cost, how long a ratchet carries it forward, and whether the utility billed what the tariff says. Load factor and energy per unit of output show how well the energy was used.
Calculations
| Quantity | How it is calculated | Units
| Total bill | Energy charges + demand charges + other charges, as entered from the bill. | currency
| Load factor | kWh / (peak kW x days x 24). Over several months: total kWh / sum of (peak x days x 24), the hours-weighted average of the monthly load factors. | %
| Blended cost | Total bill / kWh: the average price paid per kWh, demand and fees included. | currency/kWh
| Ratchet floor | The larger of: ratchet share x the highest peak in the bills of the look-back months before this one (SUMPRODUCT(MAX(...)) over earlier rows), and the minimum share x contract demand. | kW
| Billing demand | The larger of the month's own peak and the ratchet floor. | kW
| Expected demand charge | Billing demand x demand rate x share charged + fixed demand-related fees: the same formula as the Utility Demand Charge calculator. | currency
| Variance vs tariff | Billed demand charge - expected demand charge. The Check column flags it when it is more than the tolerance on Setup. | currency
| Paid for past peaks | (Billing demand - own peak) x demand rate x share charged: what an earlier peak or the contract minimum added to this bill. | currency
| Energy intensity | kWh / production. Over several months: total kWh / total production. | kWh/unit
| Cost per unit | Total bill / production. | currency/unit
| Intensity status | On target at or below the target; Near target up to 5% above; Above target beyond. | -
| Share of bill (sub-meters) | A meter's kWh / the bill's kWh for the same month. Dashboard: a meter's kWh in the 12 months / the billed kWh in the same months. | %
| Unmetered and losses | Billed kWh - the sum of the sub-meter readings in the same months. | kWh
| Cost at blended rate (est.) | A meter's kWh x the blended cost: an estimate, because demand charges are not shared out by when each load runs. | currency
Assumptions
| • | One bill per calendar month, entered on the first day of the month it covers; the ratchet looks back over whole months, so the first bills in the log have less history to look back on.
| • | The ratchet, contract minimum and rates on Setup apply to every bill in the log. If your tariff changed, the check compares old bills with the new rules: note the change on those rows.
| • | Peak demand is the meter's billed maximum demand (the utility's interval, often 15 or 30 minutes) in kW. For a kVA-billed tariff, enter kVA consistently and read kW as kVA.
| • | Production is good output in the same month as the bill.
Limitations
| • | Time-of-use energy prices, seasonal demand rates, power factor adjustments and taxes are not modelled; they are entered as part of the energy and other charge lines.
| • | The expected demand charge is only as right as the tariff rules on Setup; a flagged bill is a question for the utility, not proof of an error.
| • | Energy intensity mixes products: a shift in product mix moves kWh per unit without any change in efficiency.
| • | The Dashboard has fixed blocks for 5 sub-meters and 12 months; longer lists need the blocks extended (a warning appears on the Dashboard).
Agreement with the live calculator
The live Utility Demand Charge calculator computes one bill's demand charge from its billing demand: billing demand x rate x applicable share / 100 + fixed demand fees. The Expected demand charge column uses the same formula on every bill, after first working out the billing demand from the tariff's ratchet and contract minimum (the calculator takes billing demand as an input). The template's reference implementation is checked against the calculator's engine for its default example (920 kW, 18.50 per kW, 100%, 450 fixed: 17,470) and a ratcheted example bill on every build.
Open the Utility Demand Charge Calculator
Self-check
The Verify sheet holds fixed test inputs. Its formulas are the same formula text as the working sheets, placed against those inputs, and each result is compared with a value computed independently by the template's Python reference implementation when the file was built. If you edit a formula on a working sheet, the Verify sheet still tests the original formula text, so it will not detect your change.
Sources and standards
| • | Load factor and demand charge definitions as used in electricity tariffs and utility rate schedules; check your own tariff for its ratchet, interval and minimum-demand rules.
| • | ISO 50001:2018, Energy management systems (energy performance indicators and significant energy uses, named only).
| • | MFG Calcs Utility Demand Charge calculator (utility-demand-charge): billing demand x rate x applicable share + fixed fees.
Standards are cited by name so you can look them up; no copyrighted standard text or tables are reproduced. Statistical constants used are public.
Version history
| Version | Change | Date
| 1.0.0 | First release. | 15 October 2026
Engineering estimates for planning and improvement work. Verify the results against your own process, data and standards before you rely on them.

## Verify
Energy Use and Demand Charge Tracker
| Self-check: the workbook's formulas recomputed on fixed inputs against an independent reference. | [19 empty] | mfgcalcs.com
| Self-check status |  | PASS |  | 19 of 19 checks pass
This sheet recomputes the workbook's own formulas on fixed test inputs and compares each result with a value computed independently by the template's Python reference implementation when the file was built. Every row should read PASS. The test inputs are fixed and do not change when you edit Setup or the working sheets.
Checks
| No. | Check |  |  |  | Expected (reference) | Workbook result | Difference | Tolerance | Result
| 1 | Feb: ratchet floor = 80% of January's 1,000 kW |  |  |  | 800 | 800 | 0 | 1e-09 | PASS
| 2 | Feb: billing demand |  |  |  | 800 | 800 | 0 | 1e-09 | PASS
| 3 | Feb: paid for past peaks |  |  |  | 1850 | 1850 | 0 | 1e-09 | PASS
| 4 | Mar (calculator example): billing demand = own peak |  |  |  | 920 | 920 | 0 | 1e-09 | PASS
| 5 | Mar (calculator example): expected demand charge |  |  |  | 17470 | 17470 | 0 | 1e-09 | PASS
| 6 | Jan 2027: floor = contract minimum (January 2026 left the look-back) |  |  |  | 750 | 750 | 0 | 1e-09 | PASS
| 7 | Jan 2027: Check reports the demand charge above tariff |  |  |  | Demand charge above tariff | Demand charge above tariff |  | exact | PASS
| 8 | Jan 2026: load factor |  |  |  | 53.76% | 53.76% | 0 | 1e-09 | PASS
| 9 | Jan 2026: blended cost |  |  |  | 0.12487 | 0.12487 | 0 | 1e-09 | PASS
| 10 | Jan 2026: energy intensity |  |  |  | 1600 | 1600 | 0 | 1e-09 | PASS
| 11 | Feb: intensity status against 1,400 kWh/t |  |  |  | Near target | Near target |  | exact | PASS
| 12 | Jan 2026: intensity status |  |  |  | Above target | Above target |  | exact | PASS
| 13 | Mar: Check is OK when the bill matches |  |  |  | OK | OK |  | exact | PASS
| 14 | Window Feb 2026 - Jan 2027: total cost |  |  |  | 123220 | 123220 | 0 | 1e-09 | PASS
| 15 | Window: demand charges share |  |  |  | 39.38% | 39.38% | 0 | 1e-09 | PASS
| 16 | Window: paid for past peaks |  |  |  | 4625 | 4625 | 0 | 1e-09 | PASS
| 17 | Window: highest peak (January 2026 is outside) |  |  |  | 920 | 920 | 0 | 1e-09 | PASS
| 18 | Window: load factor |  |  |  | 59.95% | 59.95% | 0 | 1e-09 | PASS
| 19 | Window: energy intensity |  |  |  | 1523.8095 | 1523.8095 | 0 | 1e-09 | PASS
Fixed test inputs
White cells are fixed test inputs; blue cells are the workbook's formulas evaluated on them.
Parameters
| Demand charge rate |  |  | 18.5
| Share of billing demand charged |  |  | 100%
| Fixed demand-related fees |  |  | 450
| Demand ratchet |  |  | 80%
| Ratchet look-back (months) |  |  | 11
| Contract demand (kW) |  |  | 1000
| Minimum share of contract demand |  |  | 75%
| Bill check tolerance |  |  | 2%
| Load factor target |  |  | 65%
| Energy intensity target |  |  | 1400
| Window: first month |  |  | 2026-02-01
| Window: last month |  |  | 2027-01-01
Test table: Bills
[5 empty] | USD | USD | USD | t | USD | % | USD/kWh |  |  | USD | USD | USD | kWh/t | USD/t
| Month | Days | Energy (kWh) | Peak demand (kW) | Energy charges | Demand charges | Other charges | Production | Total bill | Load factor | Blended cost | Ratchet floor (kW) | Billing demand (kW) | Expected demand charge | Variance vs tariff | Paid for past peaks | Energy intensity | Cost per unit | Intensity status | Check | Notes
| 2026-01-01 | 31 | 400000 | 1000 | 30000 | 18950 | 1000 | 250 | 49950 | 53.76% | 0.12487 | 750 | 1000 | 18950 | 0 | 0 | 1600 | 199.8 | Above target | OK
| 2026-02-01 | 28 | 300000 | 700 | 22500 | 15250 | 900 | 210 | 38650 | 63.78% | 0.12883 | 800 | 800 | 15250 | 0 | 1850 | 1428.5714 | 184.0476 | Near target | OK
| 2026-03-01 | 31 | 410000 | 920 | 30750 | 17470 | 1000 | 260 | 49220 | 59.9% | 0.12005 | 800 | 920 | 17470 | 0 | 0 | 1576.9231 | 189.3077 | Above target | OK
| 2027-01-01 | 31 | 250000 | 600 | 18750 | 15800 | 800 | 160 | 35350 | 56% | 0.1414 | 750 | 750 | 14325 | 1475 | 2775 | 1562.5 | 220.9375 | Above target | Demand charge above tariff