## Start Here
Water Use Tracker
| Read this first: what the workbook does and how to use it. |  |  |  | mfgcalcs.com
Water Use Tracker
Log monthly water intake, discharge, charges and sub-meters, and see water per unit of output, cost per unit and leaks.
For: Plant, utilities and EHS managers in food and beverage, chemical and other water-intensive plants, and anyone with a water reduction target.
Version 1.0.0 · updated 15 October 2026
Quick start
| 1. | On Setup, type your plant name, currency, the volume unit your meters and bills use, your unit of output and targets, then replace the example sub-meters.
| 2. | On Monthly Water, add one row per month: intake by source, recycled water used, discharge, supply and wastewater charges, and production.
| 3. | On Sub-meters, add each meter's volume per month to see where the water goes and how much is unmetered.
| 4. | Read the Check columns: anything other than OK names the problem in words.
| 5. | Open the Dashboard; change the '12 months ending' date to look at any year.
What is in this workbook
|  | Start Here | Read this first: what the workbook does and how to use it.
|  | Setup | Plant, currency, volume unit, output unit, targets and the sub-meter list.
|  | Monthly Water | One row per month: intake by source, reuse, discharge, charges and production.
|  | Sub-meters | Water per sub-meter per month: where the water goes.
|  | Dashboard | Water intake, intensity, cost, reuse and where the water goes, for any 12 months.
|  | Method | How every number is calculated, with assumptions, limits and sources.
|  | Verify | Self-check: the workbook's formulas recomputed on fixed inputs against an independent reference.
Colour key
|  | Input | Yellow cells are yours: type a value or pick from the list. Each one says what it accepts when you click it.
|  | Calculated | Blue cells are formulas. They update as you type; overwrite one and that row stops calculating.
|  | Note | Grey boxes are guidance and labelled example data.
|  | Status words | On target / PASS / OK | Near target / Check | Below target / FAIL
Status is always written in words; the colour only repeats it, so the workbook reads the same in black-and-white print and for colour-blind readers.
Self-check and links
|  | Self-check | PASS | 18 of 18 checks pass
The Verify sheet recomputes this workbook's formulas on fixed test inputs and compares them with an independent reference calculation. PASS means every check agreed when you opened the file.
|  | Run it live | Industrial Water Cost Per Unit Calculator on mfgcalcs.com
|  | Latest version | mfgcalcs.com/templates/water-use-tracker
|  | More free templates | mfgcalcs.com/templates
|  | Version | 1.0.0 (updated 15 October 2026)
About the example data
Every number already in this workbook is example data for Kestrel Beverages, a fictional business invented for this template, so the dashboard and charts show something meaningful on day one. It covers a juice and soft drinks bottler from October 2025 to September 2026: monthly intake, discharge and charges and six sub-meters, generated from a fixed seed. Charges are example amounts, not any utility's prices. To clear it: on each working sheet, select the example rows of the table, right-click and choose Delete > Table Rows. The formulas stay, and every new row you type below the table picks them up.
Good to know
| • | Sheets Start Here, Dashboard, Method, Verify are protected without a password so formulas and layout are not overwritten by accident. To change them: Review > Unprotect Sheet.
| • | Setup and the working sheets are not protected, so tables grow as you add rows.
| • | Works in Excel 2016 and later, Microsoft 365, LibreOffice 24 and Google Sheets (File > Import). No macros, no external links, no add-ins.
| • | Money is shown in the currency you type on Setup; no exchange rates are applied.
Free from MFG Calcs - keep this credit when you share it.
Engineering estimates for planning and improvement work. Verify the results against your own process, data and standards before you rely on them.

## Setup
Water Use Tracker
| Plant, currency, volume unit, output unit, targets and the sub-meter list. |  |  | mfgcalcs.com
Plant, units and targets
| Plant name | Kestrel Beverages (example)
| Currency label | EUR
| Volume unit on the logs | m3
| m3 per volume unit | 1 | m3
| Unit of output | kL product
| Water intensity target | 2.2 | m3/kL product
| Unmetered water limit | 10%
Targets and limits are yours to set; nothing in this workbook assumes an industry benchmark. 'Near target' means within 5% of the target: up to 2.31 m3 per unit against a 2.20 target.
Sub-meters
Sub-meters (example)
One row per sub-meter or use area. The Sub-meters log reads this list; the Dashboard shows each meter's share of intake and the unmetered rest.
| Meter | Use | Notes
| Syrup and blending | Product water | Treated water into the product
| Bottle rinser | Process
| CIP | Cleaning | Clean-in-place for tanks and fillers
| Boiler make-up | Utilities
| Cooling tower | Utilities | Evaporation and blowdown
| Washrooms and canteen | Domestic

## Monthly Water
Water Use Tracker
| One row per month: intake by source, reuse, discharge, charges and production. | [19 empty] | mfgcalcs.com
Example data for Kestrel Beverages (fictional), with example charges. Replace it with your own: select the example rows, right-click, Delete > Table Rows. Volumes are in the unit chosen on Setup (row above the headers).
|  | m3 | m3 | m3 | m3 | m3 | EUR | EUR | kL product |  |  |  |  | EUR | m3/kL product | EUR/m3 | EUR/kL product | %
| Month | Mains | Groundwater | Other intake | Recycled water | Discharge | Supply charges | Wastewater charges | Production | Intake (m3) | Recycled (m3) | Discharge (m3) | Consumed (m3) | Water cost | Intensity | Cost per m3 | Cost per unit | Reuse share | Intensity status | Check | Notes
| 2025-10-01 | 6110 | 4424 | 0 | 0 | 5674 | 12074.38 | 12095.4 | 4302 | 10534 | 0 | 5674 | 4860 | 24169.78 | 2.4486 | 2.2945 | 5.6183 | 0% | Above target | OK
| 2025-11-01 | 6067 | 4394 | 0 | 0 | 5714 | 11991.23 | 12179.4 | 4219 | 10461 | 0 | 5714 | 4747 | 24170.63 | 2.4795 | 2.3105 | 5.729 | 0% | Above target | OK
| 2025-12-01 | 5949 | 4307 | 0 | 0 | 5518 | 11762.49 | 11767.8 | 4214 | 10256 | 0 | 5518 | 4738 | 23530.29 | 2.4338 | 2.2943 | 5.5838 | 0% | Above target | OK
| 2026-01-01 | 5950 | 4309 | 0 | 0 | 5546 | 11764.58 | 11826.6 | 4165 | 10259 | 0 | 5546 | 4713 | 23591.18 | 2.4631 | 2.2996 | 5.6641 | 0% | Above target | OK
| 2026-02-01 | 6114 | 4428 | 0 | 0 | 5617 | 12082.26 | 11975.7 | 4370 | 10542 | 0 | 5617 | 4925 | 24057.96 | 2.4124 | 2.2821 | 5.5053 | 0% | Above target | OK
| 2026-03-01 | 5625 | 4073 | 0 | 424 | 4980 | 11135.01 | 10638 | 4168 | 9698 | 424 | 4980 | 4718 | 21773.01 | 2.3268 | 2.2451 | 5.2239 | 4.189% | Above target | OK | CIP final-rinse recovery tank commissioned
| 2026-04-01 | 5767 | 4176 | 0 | 420 | 5110 | 11410.07 | 10911 | 4299 | 9943 | 420 | 5110 | 4833 | 22321.07 | 2.3129 | 2.2449 | 5.1922 | 4.053% | Above target | OK
| 2026-05-01 | 6123 | 4433 | 0 | 449 | 5352 | 12099.51 | 11419.2 | 4599 | 10556 | 449 | 5352 | 5204 | 23518.71 | 2.2953 | 2.228 | 5.1139 | 4.08% | Near target | OK
| 2026-06-01 | 8092 | 5860 | 0 | 538 | 7623 | 15913.4 | 16188.3 | 5145 | 13952 | 538 | 7623 | 6329 | 32101.7 | 2.7118 | 2.3009 | 6.2394 | 3.713% | Above target | OK | Leak on the buried main to the cooling tower, repaired 29 June
| 2026-07-01 | 7399 | 5358 | 0 | 541 | 6245 | 14571.11 | 13294.5 | 5262 | 12757 | 541 | 6245 | 6512 | 27865.61 | 2.4244 | 2.1843 | 5.2956 | 4.068% | Above target | OK
| 2026-08-01 | 6968 | 5046 | 420 | 530 | 6085 | 15626.32 | 12958.5 | 5119 | 12434 | 530 | 6085 | 6349 | 28584.82 | 2.429 | 2.2989 | 5.5841 | 4.088% | Above target | OK | Borehole pump failed for four days: tanker water bought
| 2026-09-01 | 5936 | 4298 | 0 | 448 | 5155 | 11737.36 | 11005.5 | 4496 | 10234 | 448 | 5155 | 5079 | 22742.86 | 2.2762 | 2.2223 | 5.0585 | 4.194% | Near target | OK

## Sub-meters
Water Use Tracker
| Water per sub-meter per month: where the water goes. | [5 empty] | mfgcalcs.com
Example data for Kestrel Beverages (fictional): six sub-meters, twelve months. Replace it with your own readings.
m3
| Month | Meter | Volume | Volume (m3) | Share of intake | Check | Notes
| 2025-10-01 | Syrup and blending | 4036 | 4036 | 38.31% | OK
| 2025-10-01 | Bottle rinser | 1262 | 1262 | 11.98% | OK
| 2025-10-01 | CIP | 2432 | 2432 | 23.09% | OK
| 2025-10-01 | Boiler make-up | 600 | 600 | 5.696% | OK
| 2025-10-01 | Cooling tower | 963 | 963 | 9.142% | OK
| 2025-10-01 | Washrooms and canteen | 504 | 504 | 4.785% | OK
| 2025-11-01 | Syrup and blending | 4065 | 4065 | 38.86% | OK
| 2025-11-01 | Bottle rinser | 1252 | 1252 | 11.97% | OK
| 2025-11-01 | CIP | 2384 | 2384 | 22.79% | OK
| 2025-11-01 | Boiler make-up | 591 | 591 | 5.65% | OK
| 2025-11-01 | Cooling tower | 918 | 918 | 8.775% | OK
| 2025-11-01 | Washrooms and canteen | 519 | 519 | 4.961% | OK
| 2025-12-01 | Syrup and blending | 3924 | 3924 | 38.26% | OK
| 2025-12-01 | Bottle rinser | 1241 | 1241 | 12.1% | OK
| 2025-12-01 | CIP | 2364 | 2364 | 23.05% | OK
| 2025-12-01 | Boiler make-up | 596 | 596 | 5.811% | OK
| 2025-12-01 | Cooling tower | 910 | 910 | 8.873% | OK
| 2025-12-01 | Washrooms and canteen | 503 | 503 | 4.904% | OK
| 2026-01-01 | Syrup and blending | 3938 | 3938 | 38.39% | OK
| 2026-01-01 | Bottle rinser | 1276 | 1276 | 12.44% | OK
| 2026-01-01 | CIP | 2293 | 2293 | 22.35% | OK
| 2026-01-01 | Boiler make-up | 598 | 598 | 5.829% | OK
| 2026-01-01 | Cooling tower | 936 | 936 | 9.124% | OK
| 2026-01-01 | Washrooms and canteen | 500 | 500 | 4.874% | OK
| 2026-02-01 | Syrup and blending | 4090 | 4090 | 38.8% | OK
| 2026-02-01 | Bottle rinser | 1286 | 1286 | 12.2% | OK
| 2026-02-01 | CIP | 2340 | 2340 | 22.2% | OK
| 2026-02-01 | Boiler make-up | 610 | 610 | 5.786% | OK
| 2026-02-01 | Cooling tower | 962 | 962 | 9.125% | OK
| 2026-02-01 | Washrooms and canteen | 516 | 516 | 4.895% | OK
| 2026-03-01 | Syrup and blending | 4033 | 4033 | 41.59% | OK
| 2026-03-01 | Bottle rinser | 1284 | 1284 | 13.24% | OK
| 2026-03-01 | CIP | 1680 | 1680 | 17.32% | OK
| 2026-03-01 | Boiler make-up | 584 | 584 | 6.022% | OK
| 2026-03-01 | Cooling tower | 944 | 944 | 9.734% | OK
| 2026-03-01 | Washrooms and canteen | 494 | 494 | 5.094% | OK
| 2026-04-01 | Syrup and blending | 4179 | 4179 | 42.03% | OK
| 2026-04-01 | Bottle rinser | 1261 | 1261 | 12.68% | OK
| 2026-04-01 | CIP | 1767 | 1767 | 17.77% | OK
| 2026-04-01 | Boiler make-up | 585 | 585 | 5.884% | OK
| 2026-04-01 | Cooling tower | 936 | 936 | 9.414% | OK
| 2026-04-01 | Washrooms and canteen | 519 | 519 | 5.22% | OK
| 2026-05-01 | Syrup and blending | 4367 | 4367 | 41.37% | OK
| 2026-05-01 | Bottle rinser | 1394 | 1394 | 13.21% | OK
| 2026-05-01 | CIP | 1808 | 1808 | 17.13% | OK
| 2026-05-01 | Boiler make-up | 662 | 662 | 6.271% | OK
| 2026-05-01 | Cooling tower | 1032 | 1032 | 9.776% | OK
| 2026-05-01 | Washrooms and canteen | 554 | 554 | 5.248% | OK
| 2026-06-01 | Syrup and blending | 4961 | 4961 | 35.56% | OK
| 2026-06-01 | Bottle rinser | 1519 | 1519 | 10.89% | OK
| 2026-06-01 | CIP | 2076 | 2076 | 14.88% | OK
| 2026-06-01 | Boiler make-up | 709 | 709 | 5.082% | OK
| 2026-06-01 | Cooling tower | 1844 | 1844 | 13.22% | OK
| 2026-06-01 | Washrooms and canteen | 611 | 611 | 4.379% | OK
| 2026-07-01 | Syrup and blending | 4919 | 4919 | 38.56% | OK
| 2026-07-01 | Bottle rinser | 1556 | 1556 | 12.2% | OK
| 2026-07-01 | CIP | 2116 | 2116 | 16.59% | OK
| 2026-07-01 | Boiler make-up | 716 | 716 | 5.613% | OK
| 2026-07-01 | Cooling tower | 1941 | 1941 | 15.22% | OK
| 2026-07-01 | Washrooms and canteen | 616 | 616 | 4.829% | OK
| 2026-08-01 | Syrup and blending | 4760 | 4760 | 38.28% | OK
| 2026-08-01 | Bottle rinser | 1559 | 1559 | 12.54% | OK
| 2026-08-01 | CIP | 2028 | 2028 | 16.31% | OK
| 2026-08-01 | Boiler make-up | 722 | 722 | 5.807% | OK
| 2026-08-01 | Cooling tower | 1897 | 1897 | 15.26% | OK
| 2026-08-01 | Washrooms and canteen | 598 | 598 | 4.809% | OK
| 2026-09-01 | Syrup and blending | 4224 | 4224 | 41.27% | OK
| 2026-09-01 | Bottle rinser | 1375 | 1375 | 13.44% | OK
| 2026-09-01 | CIP | 1761 | 1761 | 17.21% | OK
| 2026-09-01 | Boiler make-up | 626 | 626 | 6.117% | OK
| 2026-09-01 | Cooling tower | 1007 | 1007 | 9.84% | OK
| 2026-09-01 | Washrooms and canteen | 525 | 525 | 5.13% | OK

## Dashboard
Water Use Tracker
| Water intake, intensity, cost, reuse and where the water goes, for any 12 months. | [8 empty] | mfgcalcs.com
| 12 months ending |  |  |  |  | Months in the log shown |  | 12
| First month shown |  | 2025-10-01 |  |  | Last month shown |  | 2026-09-01
Volumes in m3 (converted from m3); money in EUR; output in kL product. Leave the date blank to see the latest 12 months.
| WATER INTAKE (M3) |  | INTENSITY (M3/KL PRODUCT) |  |  | WATER COST (EUR) |  |  | COST PER UNIT (EUR)
| 131626 |  | 2.4215 |  |  | 298427.62 |  |  | 5.49
| All sources, months shown |  | 2.2 |  |  | Supply plus wastewater charges |  |  | Water cost / production
Above target
| RECYCLED SHARE OF WATER USED |  | RETURNED AS WASTEWATER |  |  | COST PER M3 (EUR) |  |  | UNMETERED WATER
| 2.482% |  | 52.13% |  |  | 2.2672 |  |  | 7.953%
| Recycled / (intake + recycled) |  | Discharge / intake |  |  | Water cost / intake |  |  | 10%
On target
By month
| Month | Mains (m3) | Groundwater (m3) | Other intake (m3) | Recycled (m3) | Supply charges | Wastewater charges | Intensity | Intensity target | Unmetered
[6 empty] | EUR | EUR | m3/kL product | m3/kL product | %
| 2025-10-01 | 6110 | 4424 | 0 | 0 | 12074.38 | 12095.4 | 2.4486 | 2.2 | 6.996%
| 2025-11-01 | 6067 | 4394 | 0 | 0 | 11991.23 | 12179.4 | 2.4795 | 2.2 | 6.997%
| 2025-12-01 | 5949 | 4307 | 0 | 0 | 11762.49 | 11767.8 | 2.4338 | 2.2 | 7.001%
| 2026-01-01 | 5950 | 4309 | 0 | 0 | 11764.58 | 11826.6 | 2.4631 | 2.2 | 6.999%
| 2026-02-01 | 6114 | 4428 | 0 | 0 | 12082.26 | 11975.7 | 2.4124 | 2.2 | 7.001%
| 2026-03-01 | 5625 | 4073 | 0 | 424 | 11135.01 | 10638 | 2.3268 | 2.2 | 7.001%
| 2026-04-01 | 5767 | 4176 | 0 | 420 | 11410.07 | 10911 | 2.3129 | 2.2 | 7%
| 2026-05-01 | 6123 | 4433 | 0 | 449 | 12099.51 | 11419.2 | 2.2953 | 2.2 | 7.001%
| 2026-06-01 | 8092 | 5860 | 0 | 538 | 15913.4 | 16188.3 | 2.7118 | 2.2 | 16%
| 2026-07-01 | 7399 | 5358 | 0 | 541 | 14571.11 | 13294.5 | 2.4244 | 2.2 | 7%
| 2026-08-01 | 6968 | 5046 | 420 | 530 | 15626.32 | 12958.5 | 2.429 | 2.2 | 6.997%
| 2026-09-01 | 5936 | 4298 | 0 | 448 | 11737.36 | 11005.5 | 2.2762 | 2.2 | 6.996%
| Where the water goes (12 months shown) | [5 empty] | Unmetered water (same months)
| Sub-meter | Water (m3) | Share of intake | Per unit of output | Cost at average rate (est.) |  | Seen by the sub-meters |  |  | 121158 | m3
|  |  | % | m3/kL product | EUR |  | Unmetered and losses |  |  | 10468 | m3
| Syrup and blending | 51496 | 39.12% | 0.94735 | 116753.7471
| Bottle rinser | 16265 | 12.36% | 0.29922 | 36876.6447
| CIP | 25049 | 19.03% | 0.46082 | 56792.0734
| Boiler make-up | 7599 | 5.773% | 0.1398 | 17228.7503
| Cooling tower | 14290 | 10.86% | 0.26289 | 32398.8474
| Washrooms and canteen | 6459 | 4.907% | 0.11882 | 14644.0977
The Dashboard shows the 6 sub-meters of the Setup list. If you add more, extend the 'Where the water goes' block (see Method) or they will not appear here; the unmetered line still counts them.

## Method
Water Use Tracker
| How every number is calculated, with assumptions, limits and sources. |  | mfgcalcs.com
What this workbook calculates
Water intensity is the water a plant takes in per unit of good output. This workbook builds it month by month from the intake by source, with recycled water, discharge and the charges alongside, and converts every volume exactly to m3 from the unit on Setup. Sub-meters show where the water goes; what they do not see is unmetered water, the first place to look for leaks. Every Dashboard ratio is formed from sums, never an average of monthly ratios.
Calculations
| Quantity | How it is calculated | Units
| Volume conversion | Typed volume x m3 per unit: 1 for m3 and kL, 0.001 for L, 0.003785411784 for US gal, 0.00454609 for imp gal. | m3
| Intake | (Mains + groundwater + other intake) x m3 per unit. Recycled water is not intake. | m3
| Consumed | Intake - discharge: water that left in product, by evaporation or as losses. | m3
| Water cost | Supply charges + wastewater charges. | currency
| Intensity | Intake / production. Over several months: total intake / total production. Status: On target at or below the target, Near target up to 5% above. | m3/unit
| Cost per m3, cost per unit | Water cost / intake; water cost / production. | currency
| Reuse share | Recycled / (intake + recycled): the share of the water used that was used again. | %
| Unmetered water | (Intake - sum of the sub-meters in the same months) / intake, against the limit on Setup. | %
| Sub-meter cost (est.) | A meter's m3 x the average cost per m3: an estimate, as wastewater charges depend on where the water ends up. | currency
Assumptions
| • | One row per calendar month, entered on the first day; meter readings and bills are matched to the month they cover.
| • | Production is good output in the same month, in one unit for the whole log.
| • | All volumes on both logs are in the one unit chosen on Setup.
Limitations
| • | Water quality, treatment chemicals and energy for pumping or heating are not modelled.
| • | Intensity mixes products: a change in product mix moves m3 per unit without any change in efficiency.
| • | The Dashboard has fixed blocks for 6 sub-meters and 12 months; longer lists need the blocks extended (a warning appears).
Agreement with the live calculator
The live Industrial Water Cost Per Unit calculator divides an allocated water cost by a production volume and multiplies by an allocation factor. The Cost per unit column and tile use the same formula with a factor of 1, the month's supply plus wastewater charges over its production. The template's reference implementation is checked against the calculator's engine for its default example (48,500 over 320,000 units: 0.1516) and for one example month on every build.
Open the Industrial Water Cost Per Unit Calculator
Self-check
The Verify sheet holds fixed test inputs. Its formulas are the same formula text as the working sheets, placed against those inputs, and each result is compared with a value computed independently by the template's Python reference implementation when the file was built. If you edit a formula on a working sheet, the Verify sheet still tests the original formula text, so it will not detect your change.
Sources and standards
| • | ISO 46001:2019, Water efficiency management systems (water performance indicators, named only).
| • | CDP Water Security questionnaire and GRI 303: Water and Effluents (withdrawal, discharge and consumption definitions, named only).
| • | MFG Calcs Industrial Water Cost Per Unit calculator (industrial-water-cost-per-unit): cost / production volume x factor.
Standards are cited by name so you can look them up; no copyrighted standard text or tables are reproduced. Statistical constants used are public.
Version history
| Version | Change | Date
| 1.0.0 | First release. | 15 October 2026
Engineering estimates for planning and improvement work. Verify the results against your own process, data and standards before you rely on them.

## Verify
Water Use Tracker
| Self-check: the workbook's formulas recomputed on fixed inputs against an independent reference. | [19 empty] | mfgcalcs.com
| Self-check status |  | PASS |  | 18 of 18 checks pass
This sheet recomputes the workbook's own formulas on fixed test inputs and compares each result with a value computed independently by the template's Python reference implementation when the file was built. Every row should read PASS. The test inputs are fixed and do not change when you edit Setup or the working sheets.
Checks
| No. | Check |  |  |  | Expected (reference) | Workbook result | Difference | Tolerance | Result
| 1 | Jan (calculator example): cost per unit |  |  |  | 0.15156 | 0.15156 | 0 | 1e-09 | PASS
| 2 | Feb: intake |  |  |  | 10500 | 10500 | 0 | 1e-09 | PASS
| 3 | Feb: consumed |  |  |  | 3500 | 3500 | 0 | 1e-09 | PASS
| 4 | Feb: intensity |  |  |  | 2.2826 | 2.2826 | 0 | 1e-09 | PASS
| 5 | Feb: cost per m3 |  |  |  | 2.4952 | 2.4952 | 0 | 1e-09 | PASS
| 6 | Feb: reuse share |  |  |  | 12.5% | 12.5% | 0 | 1e-09 | PASS
| 7 | Feb: intensity status against 2.2 |  |  |  | Near target | Near target |  | exact | PASS
| 8 | Mar: intensity status (near target band) |  |  |  | On target | On target |  | exact | PASS
| 9 | Apr: Check reports discharge above intake |  |  |  | Discharge > intake: check meters | Discharge > intake: check meters |  | exact | PASS
| 10 | Sub-meter A: share of February intake |  |  |  | 57.14% | 57.14% | 0 | 1e-09 | PASS
| 11 | Window 2026: intake |  |  |  | 38500 | 38500 | 0 | 1e-09 | PASS
| 12 | Window 2026: intensity |  |  |  | 0.11724 | 0.11724 | 0 | 1e-09 | PASS
| 13 | Window 2026: cost per unit |  |  |  | 0.31227 | 0.31227 | 0 | 1e-09 | PASS
| 14 | Window 2026: reuse share |  |  |  | 3.75% | 3.75% | 0 | 1e-09 | PASS
| 15 | Window 2026: unmetered water |  |  |  | 75.32% | 75.32% | 0 | 1e-09 | PASS
| 16 | Conversion: 1 L in m3 (Setup formula) |  |  |  | 0.001 | 0.001 | 0 | 1e-09 | PASS
| 17 | Conversion: 1 US gal in m3 (Setup formula) |  |  |  | 0.0037854 | 0.0037854 | 0 | 1e-09 | PASS
| 18 | Conversion: 1 imp gal in m3 (Setup formula) |  |  |  | 0.0045461 | 0.0045461 | 0 | 1e-09 | PASS
Fixed test inputs
White cells are fixed test inputs; blue cells are the workbook's formulas evaluated on them.
Parameters
| m3 per volume unit (m3) |  |  | 1
| Water intensity target (m3/unit) |  |  | 2.2
| Window: first month |  |  | 2026-01-01
| Window: last month |  |  | 2026-12-01
| Volume unit of the test rows |  |  | m3
Test table: Water
|  | m3 | m3 | m3 | m3 | m3 | EUR | EUR | kL product |  |  |  |  | EUR | m3/kL product | EUR/m3 | EUR/kL product | %
| Month | Mains | Groundwater | Other intake | Recycled water | Discharge | Supply charges | Wastewater charges | Production | Intake (m3) | Recycled (m3) | Discharge (m3) | Consumed (m3) | Water cost | Intensity | Cost per m3 | Cost per unit | Reuse share | Intensity status | Check | Notes
| 2026-01-01 | 15000 | 5000 | 0 | 0 | 14000 | 30000 | 18500 | 320000 | 20000 | 0 | 14000 | 6000 | 48500 | 0.0625 | 2.425 | 0.15156 | 0% | On target | OK
| 2026-02-01 | 6000 | 4000 | 500 | 1500 | 7000 | 11500 | 14700 | 4600 | 10500 | 1500 | 7000 | 3500 | 26200 | 2.2826 | 2.4952 | 5.6957 | 12.5% | Near target | OK
| 2026-03-01 | 5000 | 0 | 0 | 0 | 3000 | 9000 | 6000 | 2300 | 5000 | 0 | 3000 | 2000 | 15000 | 2.1739 | 3 | 6.5217 | 0% | On target | OK
| 2026-04-01 | 3000 | 0 | 0 | 0 | 3500 | 5500 | 7350 | 1500 | 3000 | 0 | 3500 | -500 | 12850 | 2 | 4.2833 | 8.5667 | 0% | On target | Discharge > intake: check meters
Test table: Meters
| Meter | Use | Notes
| A | Process
| B | Utilities
Test table: SubMeters
m3
| Month | Meter | Volume | Volume (m3) | Share of intake | Check | Notes
| 2026-02-01 | A | 6000 | 6000 | 57.14% | OK
| 2026-02-01 | B | 3500 | 3500 | 33.33% | OK